## Slide 1
The barriers for predictive control in practice:
1. Complexity and uncertain disturbances;
More accurate prediction, adaptive control.
2. Computational speed of real time optimization;
Longer control horizon.
3. Sensor placement and data availability;
More efficient communication system (not our business), use the least amount of data.
4. (Human interaction and integration with existing systems).

## Slide 2
: capacitance of the zone, ;
: resistance to heat exchange between outdoor and envelope, ;
: cooling/heating power, ;
: solar irradiation, ;
: solar heat gain coefficient
Convert into discrete state-space form
: state vector at k+1 time instance
(Indoor temp);
: system inputs at time instance k
(Cooling load, outdoor temp);
: disturbance at time instance k (Solar irradiation and internal heat gain);
: metrics depending on sampling time (Usually obtained from linear regression).
Relatively low accuracy due to linearity;
Hard to establish RC equation if more zones;
Disturbance is hard to measure.

## Slide 3
System Identification
Nonlinear Autoregressive models with Moving Average and Exogenous Input (NARMAX):
: model output (indoor temp);
: model inputs (cooling load, outdoor temperature);
e: uncertainties and possible noise (solar and internal heat gain);
: nonlinear functions with nonlinearity degree (polynomial basis).
Polynomial basis:

## Slide 4
HP cooling load (kWh)
Outdoor T (°C)
Indoor T (°C)
Governing Equation Inferring
Polynomial basis
Nonlinear basis
FROLS
CatBoostRegressor
Parameter estimation
Measurement Inputs
Indoor T (°C)
Prediction Output
Feedback as inputs and residual estimation

## Slide 5
Predictive planning controller
HP + PCM storage
Formulate and solve optimization problem
(6 hours scheduling horizon)
Control signal
for in [0, 360, 15]
Building
Cooling energy
Indoor temperature sensor
Is the thermal comfort violated?
Real time temperature measurement
for in [0, 360, 5]
No
Follow the planning control signal
PID controller
Yes
New control signal
Local regulator
High level optimal planning solver

## Slide 6
Polynomial basis:
Time series data in
y, X1, X2
Estimate parameters, ‘E’ iteratively
Forward Regression Orthogonal Least Squares (FROLS):
Start with a set of candidate basis functions (or features) that can be used to model the system.
Iteratively select the terms that, when added to the model, provides the greatest reduction in the residual sum of squares (RSS).
At each step, use orthogonalization methods to orthogonalize the new terms with respect to the already selected terms, and evaluate the contribution of the new term.
Continue the process until a stopping criterion is met.
The final model is a linear combination of the selected nonlinear terms.
A good explanation of CatBoostRegressor:
https://towardsdatascience.com/catboost-regression-in-6-minutes-3487f3e5b329